## CDCLFOM
Linear Chemical Dose Controller/Linear Flow Orifice Meter
Item | Description | Quantity | Diameter |  | Length | Est. Unit Cost
Barbed Fittings
Barbed fitting for CHT | Durable nylon single-barbed tube fitting connecting dosing tube to CHT
Barbed fittings for drop tubes | Allows for chemical/coagulant to enter drop tube from inner diameter connector tube
Reducing barbed fittings | Connects inner diameter dosing tube to inner diameter connector tube
PVC
Drop tubes | Clear plastic such that flow is observable. Lightweight, but must ensure free fall of chemical solution
Counterweight | Small section of PVC to be used as optional counterweight to float
Tee | Used for T-shaped slider assembly for heigher flow plants
Pipe cap | Schedule 40 white PVC pipe attached to bottom of drop tubes and end of PVC-T
Square head plug | Threaded square head plug for top of float. Water tight but removable to allow weight to be added to float
Cap | Unthreaded cap for bottom of float
Pipe | Connects the adapter to PVC cap. Do not use more than necessary
Tubing
Large diameter (connector) | Clear plastic tubing to be used as a connector to the drop tube
Small diameter (dosing) | Clear plastic tubing attached to the base of the CHT and the connector tube by a reducing barbed fitting
Constant Head Tank
Plastic jar | Translucent plastic jar with hole drilled in the bottom center for the through-wall barbed fitting. Cover to prevent contamination of the chemical by particles in the ari. Small drilled hole to allow air flow.
Float and Lever System
Lever arm | Aluminum
Slider | Corrosion resistan aluminum, u-channel. Attached to the top of the lever arm to vary coagulant dose
Shaft collar | Aluminum; secured to either side of the lever arm to prevent the lever arm from displacing laterally along the shaft
Hex nut | For use between the drop tube and the slider, permits the drop tube to swing freely
Screws | One for the slider locking mechanism, one to hang the drop tube
Kerick float valve*** | Attached to side of the constant head tank to keep water level constant within CHT (***typically not available locally***)
Turnbuckle | Connects the float chain to lever-arm apparatus
Miscellaneous
Threaded adapter | Threaded adapter to receive the sqaure head plug and conver to untreaded pipe
Linear Flow Orifice Meter
PVC Pipe | Pipe for Linear Flow Orifice Meter. Drilled by uniform bit and in accordance with LFOM design algorithm to maintain linearity throughout the plant | 1 | 12 | in.

## Flocculation
S.FlocBaffle | 22.9 cm | space between baffles | Flocculation Materials
T.FlocBaffle | 2.00 mm | thickness of floc baffle
B.FlocBaffle | 23.1 cm | perpendiicular distance between baffles | Material | Size | Amount | units | Cost
H.FlocBaffleLow | 1.28 m | height of bottom baffles | Top Baffles | 1.82 m high | 25
H.FlocBaffleHigh | 1.82 m | height of top baffles | Bottom Baffles | 1.28 high | 24
S.FlocBaffleSetBackPlastic | 2.00 cm | space between floc baffles | pvc pipe (obs) | 6in (75.2 m long) (1/2 per BS) | 1767.2 | cm
N.FlocChannelBaffles | 29 | Number of flocculation channel baffles | floc spacer | 0.75 in
N.FlocFirstChannelBaffles | 21 | Number of flocculation first channel baffles
N.FlocLastChannelBaffles | 28 | Number of flocculation last channel baffles
N.FlocBaffles | 49 | Number of flocculation baffles | Material | Diameter/size | Amount | Length | Units
N.FlocChannelSpaces | 30 | Number of flocculation channel spaces | Top Baffle | 1.82 m high | 25 | N/A | N/A
ND.FlocMod | 1.27 cm (0.500 in) | Nominal diameter of flocculation module | Bottom Baffle | 1.28 m higj | 24 | N/A | N/A
PS.FlocModStr | SDR 13.5 | ???? | pvc pipe | 6 in | N/A | 1.7672 | meters
ND.FlocSpacer | 1.90 cm (0.750 in) | Nominal diameter of flocculation spacer | Floc Spacers | 0.75 in | N/A | 46.56 | meters
PS.FlocSpacerStr | SDR 17 | ????
ND.FlocObs | 15.2 cm (6.00 in) | Nominal diameter of flocculation obstacles (meaning half-pipe)?
H.FlocObs | 75.2 cm | Height of flocculation obstacles
N.FlocSpaceExpansions | 2 | Number of flocculation space expansions | 6 width*.83
N.FlocExpansions | 98 | Number of flocculation expansions
CP.FlocExpansion | 0.79 m^^(2/3) | ???? | 6*6.93
PS.FlocObsStr | SDR 41 | ????
W.FlocObstacleWake | 14.0 cm | Width of flocculation obstacle wake
N.FlocSpaceObstacles | 1 | Number of flocculation space obstacles
| 6 | Number of sedimentation tanks

## Sedimentation
Item | Diameter | Length | sdr | quantity
Outlet manifold | 6 in | 5.64 m | 41 | 6
Inlet manifold | 8 in | 5.69 m | 41 | 6
Diffusers | 1 in (square) | 15 cm each | 26 | 558
Sed Reverser | 3 in | 7.25 m | 26 | 6
Sed Plate Support | 1.50 in | 17.50 m | 26 | 6
Outlet to filter | 8 in | 2.3 m | 41 | 2
Overflow pipe | 6 in | 5 m | ? | 1
Floc Hopper drain pipe | 1 in | 1.75 m | 26 | 6
Plate spacers | .75 in | 25cm | 17 | 792
Plate spacer modules | 0.5 | 25 cm | 13.5 | 792
Accessory | Diameter of Corresponding Pipe | Quantity
Outlet manifold fitting | 6 in | 6
Outlet manifold end cap | 6 in | 6 |  |  | Diameter | Amount of Pipe (m) | SDR
Outlet manifold plug | 6 in | 6 |  |  | 0.5 in | 198 | 13.5
Inlet Manifold 90 elbow | 8 in | 6 |  |  | .75 in | 198 | 17
Inlet Manifold fitting | 8 in | 6 |  |  | 1 in | 10.5 | 26
Inlet Manifold end cap | 8 in | 6 |  |  | (Diffuser, 1in) | 83.7 | 26
Overflow T joint | 6 in | 1 |  |  | 1.5 in | 105 | 26
Overflow 90 elbow | 6 in | 1 |  |  | 3 in | 43.5 | 26
Overflow plug fitting | 6 in | 2 |  |  | 6 in | 38.84 | 41
Plate Support T Joints | 1.5 in | 22 |  |  | 8 | 38.74 | 41
Plate Support 90 elbow | 1.5 in | 4
Jet Reverser valve | 3 in | 6
Floc Hopper drain valve | 1 in | 6

## SRSF
FiAdapterPlu | 16 | Adaptor plug | N.Fi | 2 |  | Item | Nominal Diameter | Amount | Length | Width | Height
FiAuxFittingPlu | 1 | Auxillary Fitting plug elbow | H.Fi | 4.56 m | height SRSF | PVC
FiAuxPipePlu | 1 | Auxillary pipe plug | L.Fi | 1.44 m | Length SRSF | Backwash pipe | 8 in
FiAuxRemovablePlu | 1 | Auxillary removable plug | W.FiMin | 1.26 m | min width | Filter Pipe | 6in
FiBallValveGripMetalPlu | 1? | Ball valve grip metal plug | W.Fi | 1.36 m | width Srsf | Sand outlet pipe | 2 in
FiBwManWingSpacerPipe | 8 | backwsh spacer pipe | H.FiLayer | 20.0 cm | height of layers | siphon pipe | 8 in
FiChlorineDosePipePlu | 1 length:.. | chlorine dose pipe plug | ND.FiBwTrunkMax | 20.3 cm (8.00 in) | nominal diameter backwash trunk max | exit waste pipe | 4 in
FiCon |  | concrete | ND.FiTrunkMax | 15.2 cm (6.00 in) | nominal diamter of trun max | entrance overflow pipe | 6 in
FiDistFittingPlu |  | distance fitting plug | ND.FiTrunk | 15.2 cm (6.00 in) | nominal diamter of trunk | inlet channel drain | 2 in
FiDistPipePlu | 1length... | distance pipe plug | ND.FiBwTrunk | 20.3 cm (8.00 in) | nominal diameter backwash trunk | manifold branch | 1 in
FiDrainValveGripPlu | ? | drain valve grip plug | ND.FiSandOutlet | 5.08 cm (2.00 in) | nominal diameter of sand outlet | backwas manifold branch | 1.50 in
FiDrainValveMetalPlu | ? | drain valve metal plug | ND.FiSiphonAirValve | 1.90 cm (0.750 in) | siphon air valve diameter | filter branch holder | 2 in
FiEntExitFittingsPlu | 18 | enrance and exit fitting plugs | ND.FiSiphon | 20.3 cm (8.00 in) | nominal diamter of siphon pipe | filter bypass | 8 in
FiEntExitPipesPlu | 7 | entrance and exit pipe plugs | ND.FiTrunkFlushValve | 3.81 cm (1.50 in) | Nominal diameter of trunk flush valve for filter | siphon manifold oriface | 2 in | 18
FiEntranceFittingPlu | 2 | entrance fitting plug | ND.FiBwTrunkFlushValve | 5.08 cm (2.00 in) | Nominal diameter of backwash flush valve for filter | manifold branch |  | 28 | 56 cm
FiFlexCouplingPlu | 6 | flex coupling plug | ND.FiExitWaste | 10.2 cm (4.00 in) | Nominal diameter of exit waste pipe for filter | backwash manifold branch |  |  | 53.5
FiInletChannelCon |  |  | ND.FiEntOverflow | 15.2 cm (6.00 in) | Nominal diameter entrance overflow for filter | manifold oriface bw |  | 140(5 per branch) |  | 5 per branch
Material: Plastic Sheet (weir)
FiInletChannelDrainFittingPlu | 1 | inlet channel drain fitting plug | ND.FiInletChannelDrain | 5.08 cm (2.00 in) | Nominal diameter of inlet channel drain for filter | Stop Gate |  |  | 72.1 cm width |  | 20 cm
FiInletChannelDrainPipePlu | 1 | inlet channel drain pipe plug | ND.FiManBranch | 2.54 cm (1.00 in) | Nominal diameter of manifold branch for filter (main layer) | slot stopper |  | 3 |  |  | 70.8 cm
FiInletChannelDrainRemovablePlu | 1 | inlet channel drain removable plug | ND.FiBwManBranch | 3.81 cm (1.50 in) | Nominal diameter of backwash manifold branch (backwash layer) | Material: Valves
FiManBranchPlu | 336 | man branch plug | ND.FiBranchHolder | 5.08 cm (2.00 in) | Nominal diameter of branch holder for filter | siphon air valve | 0.750 in
FiManCapPlu | 8 small | 2 big | ND.FiBypass | 20.3 cm (8.00 in) | Nominal diameter of filter bypass | backwash flush valve | 2 in
FiManPipePlu | 4 small | 2 big | B.FiSiphonManOrifices | 6.68 cm | Perpendicular distance between siphon manifold orifices in filter | flush valve | 1.5 in
FiManWingSpacerPipe | 8 | spacer pipe | N.FiSiphonManOrifices | 18 | Number of siphon manifold orifices
FiManWingSpacerTee | 8 | spacer tee | D.FiSiphonManOrifices | 5.08 cm (2.00 in) | diameter of siphon manifold orifices in filter
FiOverflowDistBoxCon |  |  | N.FiManBranch | 28 | Number of manifold branches for filter
FiReducerPlu | 6 | reducer plug | L.FiBwManBranch | 53.5 cm | Length of manifold branch (backwash layer)
FiRemovableBaffle | 2(4) | removable baffles (weirs) | L.FiManBranch | 56.0 cm | Length of manifold branch (main layer)
FiRemovablePlu | 14 | removable plugs | L.FiManBranchExt | 2.00 cm | Exterior length of manifold branch
FiSandDrainAdapterPlu | 2 | sand drain adaptor plug | A.FiBwManOrificesEst | 0.0201 m^^2 | Estimated area of manifold orifices in backwash
FiSandDrainFittingPlu | 4 | sand drain fitting plug | N.FiBwManOrifices | 140 | Number of manifold orifices in backwash
FiSandDrainPipePlu | 2 | sand drain pipe plug | N.FiBwManOrificesPerBranch | 5 | Number of manifold orifices per branch in backwash
FiSandDrainValvePlu | 1? | sand drain valve pluf | D.FiBwManOrifice | 1.27 cm (0.500 in) | Diameter of siphon manifold orifices in filter
FiSiphonAirValvePlu | 1? | siphon air valve plug | B.FiBwManOrifice | 11.1 cm
FiSiphonFittingPlu | 10 | siphon fitting plug | N.FiInletManOrifices | 196
FiSiphonPipePlu | 2 (4 sieve) | siphone pipe plug] | N.FiInletManOrificesPerBranch | 7
FiTankCon |  |  | D.FiInletManOrifice | 1.59 cm (0.625 in)
FiValvePlu |  | valve plug | B.FiManOrificeEst | 5.00 cm | number of inlet man orifices
|  |  | B.FiInletManOrifice | 7.83 cm | number of man orificese per branch
|  |  | N.FiTopManOrifices | 140
|  |  | N.FiTopManOrificesPerBranch | 5
|  |  | D.FiTopManOrifice | 1.27 cm (0.500 in)
|  |  | B.FiTopManOrifice | 11.7 cm | number of inlet manorifices forward
|  |  | L.FiOutletBranchSlotted | 51.7 cm | diameter of top man oriface
|  |  | N.FiSlotRows | 2
|  |  | W.FiManSlots | 203 microm
|  |  | B.FiManSlot | 3.17 mm | length of outlet branch
|  |  | N.FiOutletManSlotsPerRow | 162 | number of slot rows
|  |  | N.FiOutletManSlotsPerBranch | 324 | width of man slots
|  |  | L.FiOutletManSlotCurvedInner | 2.18 cm
|  |  | A.FiOutletManSlots | 0.0402 m^^2 | number of outlet manslots per row
|  |  | Pi.QFiBw | 1.15 | number of outlet man slots per branch
|  |  | H.FiStopGate | 20.0 cm | length of outlet man slot curved inner
|  |  | W.FiStopGate | 72.1 cm | area outlet man slots
|  |  | W.FiBwFlowControl | 3.40 cm
|  |  | H.FiFlowControlSlotTotal | 70.8 cm | height of stop gate
|  |  | H.FiSlotStopper | 3.00 cm | width of flow control
|  |  | N.FiSlotStopper | 3 | height of flow control slot total
|  |  | D.FiSandES | 500 microm (0.0197 in)
|  |  | D.FiSand60 | 825 microm (0.0325 in)
|  |  | Vol.FiSand | 4.17 kL